## Calculator
FG-NET / FG-BBOX Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 3 registers per cable (select function)
- Alarm type: Show leak and breaks
- Alarm state: Show if the alarm is new, or seen, or acknowledged, or ejected
- Alarm location: Show the location in meters of leak alarms
- Register type: depends of the function
Protocol |  | Panel |  | Circuit | Cable | Function |  |  | Register | Register type
MODBUS | 1 | FG-NET | 0 | 1 | 1 | Alarm type | 7 | 10 | 7102 | 1
JBUS |  | FG-NET | 0 | 1 | 1 | Alarm type
MODBUS |  | FG-BBOX #01 | 01 | 2 | 2 | Alarm state
|  | FG-BBOX #02 | 02 | 3 | 3 | Alarm location
|  | FG-BBOX #03 | 03 |  | 4
|  | FG-BBOX #04 | 04 |  | 5
|  | FG-BBOX #05 | 05 |  | 6
|  | FG-BBOX #06 | 06 |  | 7
|  | FG-BBOX #07 | 07 |  | 8
|  | FG-BBOX #08 | 08 |  | 9
|  | FG-BBOX #09 | 09 |  | 10
|  | FG-BBOX #10 | 10 |  | 11
|  | FG-BBOX #11 | 11 |  | 12
|  | FG-BBOX #12 | 12 |  | 13
|  | FG-BBOX #13 | 13 |  | 14
|  | FG-BBOX #14 | 14 |  | 15
|  | FG-BBOX #15 | 15 |  | 16
|  | FG-BBOX #16 | 16 |  | 17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
Additional registers
Global register
- Show all leaks, all breaks anywhere on the system
- Show communication trouble with any satellite box
- Register type 4
Protocol |  | Register
MODBUS | 1 | 4097
Global registers per circuit
- Show all leaks, all breaks anywhere on a circuit
- Register type 5
Protocol |  | Panel |  | Circuit | Register
MODBUS | 1 | FG-NET | -1 | 1 | 4098
1
2
3
Satellites communication registers
- Show if a satellite box is enabled or disabled
- Show if an enabled satellite is online or offline
- Register type 6
Protocol |  | Panel |  | Register
MODBUS | 1 | FG-BBOX #01 | 01 | 4202
FG-BBOX #01
FG-BBOX #02
FG-BBOX #03
FG-BBOX #04
FG-BBOX #05
FG-BBOX #06
FG-BBOX #07
FG-BBOX #08
FG-BBOX #09
FG-BBOX #10
FG-BBOX #11
FG-BBOX #12
FG-BBOX #13
FG-BBOX #14
FG-BBOX #15
FG-BBOX #16
FG-RELAYS #01
FG-RELAYS #02
FG-RELAYS #03
FG-RELAYS #04
FG-RELAYS #05
FG-RELAYS #06
FG-RELAYS #07
FG-RELAYS #08
FG-RELAYS #09
FG-RELAYS #10
FG-RELAYS #11
FG-RELAYS #12
FG-RELAYS #13
FG-RELAYS #14
FG-RELAYS #15
FG-RELAYS #16

## Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | CABLE BREAK END PLUG | CABLE BREAK SENSOR | CABLE BREAK BUS
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | EJECTED | ACKED | SEEN | NEW
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LOCATION (in meters, associated values)
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | EXTERNAL DEVICES OFFLINE
BITS POSITION IN TYPE 5 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 6 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | DEVICE DISABLED | EXTERNAL DEVICE OFFLINE