## INSTALLATION TABLE
Project : | Add Project Name here
Subject:BMS integration points with TTK Leak Detection System
PANEL TYPE : FG-NET
Location : | Add Panel Location here
IP Address : | XXX.XXX.XXX.XXX
PROTOCOL : MODBUS TCP port 502 and/or, Serial MODBUS RTU. Use ONE SERIAL INTERFACE ONLY, RS232 OR RS422 OR RS485 RS 232: Use 3 points terminal and crossover cable RS 422: Use 4 points terminal and crossover cable RS 485: Use 4 points terminal and loop Rx- with Tx- for DATA-, and Rx+ with Tx+ for DATA+
BAUDRATE : 9600 (can't be changed)
PARITY : NO (can't be changed)
STOP BIT: 1 BIT STOP, 8 DATA BITS (can't be changed)
SLAVE NUMBER can be set from 1 to 247
|  |  |  | TYPE INFORMATION |  |  |  |  | STATE INFORMATION |  |  |  |  | LOCATION (m)
CABLE NUMBER | DESCRIPTION | CABLE NAME SET ON PANEL | DEVICE ID (SLAVE NO) | TYPE REGISTER ADDRESS | TYPE BIT POSITION |  |  |  | STATE REGISTER ADDRESS | STATE BIT POSITION |  |  |  | LOCATION REGISTER ADDRESS | LOCATION BIT POSITION | REMARKS
[5 empty] | LEAK | CABLE BREAK BUS | CABLE BREAK SENSOR | CABLE BREAK END PLUG |  | NEW | SEEN | ACKED | EJECTED |  | LOCATION (m)
CIRCUIT 1 (up to 40 cables from 1_01 to 1_40)
1_01 | CABLE 1_01 |  | 1 | 7101 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8101 | bit 0 | bit 1 | bit 2 | bit 3 | 9101 | bits 0 to 15
1_02 | CABLE 1_02 |  | 1 | 7102 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8102 | bit 0 | bit 1 | bit 2 | bit 3 | 9102 | bits 0 to 15
1_03 | CABLE 1_03 |  | 1 | 7103 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8103 | bit 0 | bit 1 | bit 2 | bit 3 | 9103 | bits 0 to 15
1_04 | CABLE 1_04 |  | 1 | 7104 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8104 | bit 0 | bit 1 | bit 2 | bit 3 | 9104 | bits 0 to 15
1_05 | CABLE 1_05 |  | 1 | 7105 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8105 | bit 0 | bit 1 | bit 2 | bit 3 | 9105 | bits 0 to 15
1_06 | CABLE 1_06 |  | 1 | 7106 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8106 | bit 0 | bit 1 | bit 2 | bit 3 | 9106 | bits 0 to 15
1_07 | End Plug |  | 1 | 7107 | N/A | N/A | N/A | bits 2+7 | 8107 | bit 0 | bit 1 | bit 2 | bit 3 | 9107 | N/A | Will code Break End of Circuit fault only
CIRCUIT 2 (up to 40 cables from 2_01 to 2_40)
2_01 | CABLE 2_01 |  | 1 | 7201 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8201 | bit 0 | bit 1 | bit 2 | bit 3 | 9201 | bits 0 to 15
2_02 | CABLE 2_02 |  | 1 | 7202 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8202 | bit 0 | bit 1 | bit 2 | bit 3 | 9202 | bits 0 to 15
2_03 | CABLE 2_03 |  | 1 | 7203 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8203 | bit 0 | bit 1 | bit 2 | bit 3 | 9203 | bits 0 to 15
2_04 | CABLE 2_04 |  | 1 | 7204 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8204 | bit 0 | bit 1 | bit 2 | bit 3 | 9204 | bits 0 to 15
2_05 | CABLE 2_05 |  | 1 | 7205 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8205 | bit 0 | bit 1 | bit 2 | bit 3 | 9205 | bits 0 to 15
2_06 | End Plug |  | 1 | 7206 | N/A | N/A | N/A | bits 2+7 | 8206 | bit 0 | bit 1 | bit 2 | bit 3 | 9206 | N/A | Will code Break End of Circuit fault only
CIRCUIT 3 (up to 40 cables from 3_01 to 3_40)
3_01 | CABLE 3_01 |  | 1 | 7301 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8301 | bit 0 | bit 1 | bit 2 | bit 3 | 9301 | bits 0 to 15
3_02 | CABLE 3_02 |  | 1 | 7302 | bit 4 | bits 0+7 | bits 1+7 | N/A | 8302 | bit 0 | bit 1 | bit 2 | bit 3 | 9302 | bits 0 to 15
3_03 | End plug |  | 1 | 7303 | N/A | N/A | N/A | bits 2+7 | 8303 | bit 0 | bit 1 | bit 2 | bit 3 | 9303 | N/A | Will code Break End of Circuit fault only
CABLE INFORMATION TYPE: Types can be Leaks, or Cable Break Bus (communication loss), or Cable Break Sensor (only the sensing part), or Cable Break End of Circuit (missing end plug), bit 7 is a common fault for these three Cable Breaks, show this register in Binary. STATE: States can be New, or Seen, or Acknowledged, or Ejected. When a cable is ejected, the TYPE and LOCATION Registers won't code alarms anymore, show this register in Binary. LOCATION: Locations are given in meters, the system will return a 0 value when there is no alarm, associations will affect this value and the location is always given as per the panel display (I.E. 587 meters), show this register in Decimal. CHECK SECOND SHEET FOR BITS LAYOUT
ADDITIONAL REGISTERS 4096 FOR SYSTEM GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on the Panel 4097 FOR CIRCUIT 1 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 1 4098 FOR CIRCUIT 2 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 2 4099 FOR CIRCUIT 3 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 3 CHECK SECOND SHEET FOR BITS LAYOUT | [8 empty] | CHARSET MANAGMENT: SHIFT REGISTER ADDRESS AT N+1 All addresses are given as per the real addresses in our system, but due to the charset managment of some BMS systems, the starting address might be shifted of one additional register. In this case, the TYPE address for CABLE 1_01 will be 7102 (7101 + 1). This situation will be the same for all registers.

## BITS LAYOUT
BITS POSITION IN TYPE REGISTERS (7000 series)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | CABLE BREAK END PLUG | CABLE BREAK SENSOR | CABLE BREAK BUS
BITS POSITION IN STATE REGISTERS (8000 series)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | EJECTED | ACKED | SEEN | NEW
BITS POSITION IN LOCATION REGISTERS (9000 series)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LOCATION (in meters)
BITS POSITION IN ADDITIONAL REGISTERS (4096 to 4099)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED