## INSTALLATION TABLE
Project : | Add Project Name here
Subject:BMS integration points with TTK Leak Detection System
PANEL TYPE : FG-SYS
Location : | Add Panel Location here
PROTOCOL : Serial MODBUS RTU, 2 independant interfaces. RS 232: Use 3 points terminal and crossover cable RS 422: Use 4 points terminal and crossover cable RS 485: Use 4 points terminal and loop Rx- with Tx- for DATA-, and Rx+ with Tx+ for DATA+
BAUDRATE : 9600 (can't be changed)
PARITY : NO (can't be changed)
STOP BIT: 1 BIT STOP, 8 DATA BITS (can't be changed)
SLAVE NUMBER can be set from 1 to 247
|  |  |  | TYPE INFORMATION (7000 series) |  |  |  |  | STATE INFORMATION (8000 series) | LOCATION (m) (9000 series)
CABLE NUMBER | DESCRIPTION | CABLE NAME SET ON PANEL | DEVICE ID (SLAVE NO) | TYPE REGISTER ADDRESS | TYPE BIT POSITION |  |  |  | NOT AVAILABLE ON FG-SYS | LOCATION REGISTER ADDRESS | LOCATION BIT POSITION | REMARKS
[5 empty] | LEAK | CABLE BREAK BUS | CABLE BREAK SENSOR | CABLE BREAK END PLUG |  |  | LOCATION (m)
CIRCUIT 1 (up to 40 cables from 1 to 40)
1 | CABLE 1 |  | 1 | 7101 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9101 | bits 0 to 15
2 | CABLE 2 |  | 1 | 7102 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9102 | bits 0 to 15
3 | CABLE 3 |  | 1 | 7103 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9103 | bits 0 to 15
4 | CABLE 4 |  | 1 | 7104 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9104 | bits 0 to 15
5 | CABLE 5 |  | 1 | 7105 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9105 | bits 0 to 15
6 | CABLE 6 |  | 1 | 7106 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9106 | bits 0 to 15
7 | End Plug |  | 1 | 7107 | N/A | N/A | N/A | bits 2+7 |  | 9107 | N/A | Will code Break End of Circuit fault only
CIRCUIT 2 (up to 40 cables from 61 to 100)
61 | CABLE 61 |  | 1 | 7201 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9201 | bits 0 to 15
62 | CABLE 62 |  | 1 | 7202 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9202 | bits 0 to 15
63 | CABLE 63 |  | 1 | 7203 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9203 | bits 0 to 15
64 | CABLE 64 |  | 1 | 7204 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9204 | bits 0 to 15
65 | CABLE 65 |  | 1 | 7205 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9205 | bits 0 to 15
66 | End Plug |  | 1 | 7206 | N/A | N/A | N/A | bits 2+7 |  | 9206 | N/A | Will code Break End of Circuit fault only
CIRCUIT 3 (up to 40 cables from 121 to 160)
121 | CABLE 121 |  | 1 | 7301 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9301 | bits 0 to 15
122 | CABLE 122 |  | 1 | 7302 | bit 4 | bits 0+7 | bits 1+7 | N/A |  | 9302 | bits 0 to 15
123 | End plug |  | 1 | 7303 | N/A | N/A | N/A | bits 2+7 |  | 9303 | N/A | Will code Break End of Circuit fault only
CABLE INFORMATION TYPE: Types can be Leaks, or Cable Break Bus (communication loss), or Cable Break Sensor (only the sensing part), or Cable Break End of Circuit (missing end plug), bit 7 is a common fault for these three Cable Breaks, show this register in Binary. LOCATION: Locations are given in meters, the system will return a 0 value when there is no alarm, associations will affect this value and the location is always given as per the panel display (I.E. 587 meters), show this register in Decimal. CHECK SECOND SHEET FOR BITS LAYOUT
ADDITIONAL REGISTERS 4096 FOR SYSTEM GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on the Panel 4097 FOR CIRCUIT 1 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 1 4098 FOR CIRCUIT 2 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 2 4099 FOR CIRCUIT 3 GLOBAL STATUS, this will show if there is any Leak or Cable Break anywhere on Circuit 3 CHECK SECOND SHEET FOR BITS LAYOUT | [8 empty] | CHARSET MANAGMENT: SHIFT REGISTER ADDRESS AT N+1 All addresses are given as per the real addresses in our system, but due to the charset managment of some BMS systems, the starting address might be shifted of one additional register. In this case, the TYPE address for CABLE 1_01 will be 7102 (7101 + 1). This situation will be the same for all registers.

## BITS LAYOUT
BITS POSITION IN TYPE REGISTERS (7000 series)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | CABLE BREAK END PLUG | CABLE BREAK SENSOR | CABLE BREAK BUS
BITS POSITION IN LOCATION REGISTERS (9000 series)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LOCATION (in meters)
BITS POSITION IN ADDITIONAL REGISTERS (4096 to 4099)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED