## FG-NET Calculator
FG-NET / FG-BBOX Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 3 registers per cable (select function)
- Alarm type: Show leak and breaks
- Alarm state: Show if the alarm is new, or seen, or acknowledged, or ejected
- Alarm location: Show the location in meters of leak alarms
- Register type: depends of the function
Protocol |  | Panel |  | Circuit | Cable | Function |  |  | Register | Register type
MODBUS | 1 | FG-NET | 0 | 1 | 1 | Alarm type | 7 | 10 | 7102 | 1
JBUS |  | FG-NET | 0 | 1 | 1 | Alarm type
MODBUS |  | FG-BBOX #01 | 01 | 2 | 2 | Alarm state
|  | FG-BBOX #02 | 02 | 3 | 3 | Alarm location
|  | FG-BBOX #03 | 03 |  | 4
|  | FG-BBOX #04 | 04 |  | 5
|  | FG-BBOX #05 | 05 |  | 6
|  | FG-BBOX #06 | 06 |  | 7
|  | FG-BBOX #07 | 07 |  | 8
|  | FG-BBOX #08 | 08 |  | 9
|  | FG-BBOX #09 | 09 |  | 10
|  | FG-BBOX #10 | 10 |  | 11
|  | FG-BBOX #11 | 11 |  | 12
|  | FG-BBOX #12 | 12 |  | 13
|  | FG-BBOX #13 | 13 |  | 14
|  | FG-BBOX #14 | 14 |  | 15
|  | FG-BBOX #15 | 15 |  | 16
|  | FG-BBOX #16 | 16 |  | 17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
Additional registers
Global register
- Show all leaks, all breaks anywhere on the system
- Show communication trouble with any satellite box
- Register type 4
Protocol |  | Register
MODBUS | 1 | 4097
Global registers per circuit
- Show all leaks, all breaks anywhere on a circuit
- Register type 5
Protocol |  | Panel |  | Circuit | Register
MODBUS | 1 | FG-NET | -1 | 1 | 4098
1
2
3
Satellites communication registers
- Show if a satellite box is enabled or disabled
- Show if an enabled satellite is online or offline
- Register type 6
Protocol |  | Panel |  | Register
MODBUS | 1 | FG-BBOX #01 | 01 | 4202
FG-BBOX #01
FG-BBOX #02
FG-BBOX #03
FG-BBOX #04
FG-BBOX #05
FG-BBOX #06
FG-BBOX #07
FG-BBOX #08
FG-BBOX #09
FG-BBOX #10
FG-BBOX #11
FG-BBOX #12
FG-BBOX #13
FG-BBOX #14
FG-BBOX #15
FG-BBOX #16
FG-RELAYS #01
FG-RELAYS #02
FG-RELAYS #03
FG-RELAYS #04
FG-RELAYS #05
FG-RELAYS #06
FG-RELAYS #07
FG-RELAYS #08
FG-RELAYS #09
FG-RELAYS #10
FG-RELAYS #11
FG-RELAYS #12
FG-RELAYS #13
FG-RELAYS #14
FG-RELAYS #15
FG-RELAYS #16

## FG-NET Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | CABLE BREAK END PLUG | CABLE BREAK SENSOR | CABLE BREAK BUS
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | EJECTED | ACKED | SEEN | NEW
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LOCATION (in meters, associated values)
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | EXTERNAL DEVICES OFFLINE
BITS POSITION IN TYPE 5 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 6 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | DEVICE DISABLED | EXTERNAL DEVICE OFFLINE

## FG-SYS (2014) Calculator
FG-SYS (2014) Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 2 registers per cable (select function)
- Alarm type: Show leak and breaks
- Alarm location: Show the location in meters of leak alarms
- Register type: depends of the function
Protocol |  | Panel |  | Circuit | Cable | Function |  |  | Register | Register type
MODBUS | 1 | FG-SYS | 0 | 1 | 1 | Alarm type | 7 | 10 | 7102 | 1
JBUS |  | FG-NET | 0 | 1 | 1 | Alarm type
MODBUS |  | FG-BBOX #01 | 01 | 2 | 2 | Alarm location
|  | FG-BBOX #02 | 02 | 3 | 3 | Alarm location
|  | FG-BBOX #03 | 03 |  | 4
|  | FG-BBOX #04 | 04 |  | 5
|  | FG-BBOX #05 | 05 |  | 6
|  | FG-BBOX #06 | 06 |  | 7
|  | FG-BBOX #07 | 07 |  | 8
|  | FG-BBOX #08 | 08 |  | 9
|  | FG-BBOX #09 | 09 |  | 10
|  | FG-BBOX #10 | 10 |  | 11
|  | FG-BBOX #11 | 11 |  | 12
|  | FG-BBOX #12 | 12 |  | 13
|  | FG-BBOX #13 | 13 |  | 14
|  | FG-BBOX #14 | 14 |  | 15
|  | FG-BBOX #15 | 15 |  | 16
|  | FG-BBOX #16 | 16 |  | 17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
Additional registers
Global register
- Show all leaks, all breaks anywhere on the system
- Register type 3
Protocol |  | Register
MODBUS | 1 | 4097
Global registers per circuit
- Show all leaks, all breaks anywhere on a circuit
- Register type 3
Protocol |  | Panel |  | Circuit | Register
MODBUS | 1 | FG-SYS | -1 | 1 | 4098
1
2
3 --> N/A

## FG-SYS (2014) Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | CABLE BREAK END PLUG | CABLE BREAK SENSOR | CABLE BREAK BUS
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LOCATION (in meters, associated values)
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED

## FG-SYS (old) Calculator
FG-SYS (old) Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 2 cables in each register
Protocol |  | Panel | Circuit |  | Cable | Byte address | Register address | LSB/MSB | Register type
MODBUS | 1 | FG-SYS | 1 | 1952 | 1 | 1953 | 1952.5 | MSB | 1
JBUS |  | FG-NET | 1 | 0 | 1
MODBUS |  | FG-BBOX #01 | 2 | 01 | 2
|  | FG-BBOX #02 | 3 | 02 | 3
|  | FG-BBOX #03 |  | 03 | 4
|  | FG-BBOX #04 |  | 04 | 5
|  | FG-BBOX #05 |  | 05 | 6
|  | FG-BBOX #06 |  | 06 | 7
|  | FG-BBOX #07 |  | 07 | 8
|  | FG-BBOX #08 |  | 08 | 9
|  | FG-BBOX #09 |  | 09 | 10
|  | FG-BBOX #10 |  | 10 | 11
|  | FG-BBOX #11 |  | 11 | 12
|  | FG-BBOX #12 |  | 12 | 13
|  | FG-BBOX #13 |  | 13 | 14
|  | FG-BBOX #14 |  | 14 | 15
|  | FG-BBOX #15 |  | 15 | 16
|  | FG-BBOX #16 |  | 16 | 17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
PLEASE HELP ME
- Enter the quantity of cables for each circuit
- We will add one Byte for the end plug
Circuit 1 |  | Circuit 2 | Circuit 3
|  |  | Starting address |  | Length
Circuit 1 |  | 1st poll
2nd poll
Circuit 2 |  | 1st poll
2nd poll
Circuit 3 |  | 1st poll
2nd poll

## FG-SYS (old) Register types
BITS POSITION IN TYPE 1 REGISTERS
MSB (odd cable) | [7 empty] | LSB (even cable)
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | LOCATION (in meters) |  |  |  | CABLE BREAK (ALL TYPES) | UNUSED | UNUSED | LEAK | LOCATION (in meters)

## FG-ALS8 Calculator
FG-ALS8 Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Caution : 16 registers per request max.
Cables registers
- 4 registers per zone
- Installed length
- Leak information
- Break information
- Location (Leak location in meters / Break location is always 1)
- Register type: depends of the information
Protocol |  | Panel | Zone | Information | Register | Register type
MODBUS | 1 | FG-ALS8 | 1 | Installed length | 1 | 1
JBUS |  |  | 1 | Installed length
MODBUS |  |  | 2 | Leak information
|  |  | 3 | Break information
|  |  | 4 | Leak location
5
6
7
8

## FG-ALS8 Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (in meters) OR BREAK LOCATION (always at 1)

## FG-ALS8-OD Calculator
FG-ALS8 Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Caution : 16 registers per request max.
Cables registers
- 4 registers per zone
- Installed length
- Leak information
- Break information
- Location (Leak location is always 1 / Break location is always 0)
- Register type: depends of the information
Protocol |  | Panel | Zone | Information | Register | Register type
MODBUS | 1 | FG-ALS8-OD | 1 | Installed length | 1 | 1
JBUS |  |  | 1 | Installed length
MODBUS |  |  | 2 | Leak information
|  |  | 3 --> N/A | Break information
|  |  | 4 | Leak location
5
6
7
8

## FG-ALS8-OD Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK (ALL TYPES) | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK SENSOR | BREAK BUS or BREAK END
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (always at 1) OR BREAK LOCATION (always at 0)

## FG-ALS4 Calculator
FG-ALS4 Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 4 registers per zone
- Installed length
- Leak information
- Break information
- Location (Leak location in meters / Break location is always 1)
- Register type: depends of the information
Protocol |  | Panel | Zone | Information | Register | Register type
MODBUS | 1 | FG-ALS4 | 1 | Installed length | 1 | 1
JBUS |  |  | 1 | Installed length
MODBUS |  |  | 2 | Leak information
|  |  | 3 | Break information
|  |  | 4 | Leak location

## FG-ALS4 Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (in meters) OR BREAK LOCATION (always at 1)

## FG-ALS4-OD Calculator
FG-ALS4-OD Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 4 registers per zone
- Installed length
- Leak information
- Break information
- Location (Leak location is always 1 / Break location is always 0)
- Register type: depends of the information
Protocol |  | Panel | Zone | Information | Register | Register type
MODBUS | 1 | FG-ALS4-OD | 1 | Installed length | 1 | 1
JBUS |  |  | 1 | Installed length
MODBUS |  |  | 2 | Leak information
|  |  | 3 --> N/A | Break information
|  |  | 4 | Leak location

## FG-ALS4-OD Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK (ALL TYPES) | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK SENSOR | BREAK BUS or BREAK END
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (always at 1) OR BREAK LOCATION (always at 0)

## FG-ALS Calculator
FG-ALS Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 4 registers
- Installed length
- Leak information
- Break information
- Location (Leak location in meters / Break location is always 1)
- Register type: depends of the information
Protocol |  | Panel | Information | Register | Register type
MODBUS | 1 | FG-ALS | Installed length | 1 | 1
JBUS |  |  | Installed length
MODBUS |  |  | Leak information
Break information
Leak location

## FG-ALS Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (in meters) OR BREAK LOCATION (always at 1)

## FG-ALS Dip Switch Configurator
Enter the slave number : |  |  |  |  | 0
0
Result :
|  | ON | [5 empty] | DIP
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FG-A (future) Calculator
FG-A Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 4 registers
- Installed length
- Leak information
- Break information
- Location (Leak location in meters / Break location is always 1)
- Register type: depends of the information
Protocol |  | Panel | Information | Register | Register type
MODBUS | 1 | FG-A | Installed length | 1 | 1
JBUS |  |  | Installed length
MODBUS |  |  | Leak information
Break information
Leak location

## FG-A (future) Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (in meters) OR BREAK LOCATION (always at 1)

## FG-A (future) Dip Switch Config
Enter the slave number : |  |  |  |  | 0
0
Result :
|  | ON | [5 empty] | DIP
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FG-A-OD (future) Calculator
FG-A-OD Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Cables registers
- 4 registers
- Installed length
- Leak information
- Break information
- Location (Leak location is always 1 / Break location is always 0)
- Register type: depends of the information
Protocol |  | Panel | Information | Register | Register type
MODBUS | 1 | FG-A-OD | Installed length | 1 | 1
JBUS |  |  | Installed length
MODBUS |  |  | Leak information
Break information
Leak location

## FG-A-OD (future) Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK (ALL TYPES) | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK SENSOR | BREAK BUS or BREAK END
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (always at 1) OR BREAK LOCATION (always at 0)

## FG-A-OD (future) Dip Switch Cfg
Enter the slave number : |  |  |  |  | 0
0
Result :
|  | ON | [5 empty] | DIP
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FG-ALB Calculator
FG-ALB Modbus registers calculator
Check the second sheet for register types
Select values in grey cells
Caution : 16 registers per request max.
Cables registers
- 4 registers per zone
- Installed length
- Leak information
- Break information
- Leak location
- Register type: depends of the information
Protocol |  | Panel | Cable | Information | Register | Register type
MODBUS | 1 | FG-ALB | 1 | Installed length | 1 | 1
JBUS |  |  | 1 | Installed length
MODBUS |  |  | 2 | Leak information
|  |  | 3 | Break information
|  |  | 4 | Leak location
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30

## FG-ALB Register types
BITS POSITION IN TYPE 1 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
INSTALLED LENGTH (in meters)
BITS POSITION IN TYPE 2 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | LEAK | UNUSED | UNUSED | UNUSED | UNUSED
BITS POSITION IN TYPE 3 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | UNUSED | BREAK
BITS POSITION IN TYPE 4 REGISTERS
15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
LEAK LOCATION (in meters)

## FG-DI Dip Switch Configurator
Enter the slave number : |  |  |  |  | 0
Enter the number of enabled Digital Inputs : | [7 empty] | 0
Select the Mode : |  |  |  | N.C.
0
| SW1 | [8 empty] | SW2
|  | ON | [5 empty] | DIP |  |  | ON | [6 empty] | DIP
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | 1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N.O. | N.C. | x |  | 0 | 0 | 0 | 0 | 0 | 0

## FG-DTM Dip Switch Configurator
Enter the number of enabled outputs : | [5 empty] | 0
0
Result :
|  | ON |  | DIP
|  | 0 | 0 | 0 | 0
|  | 1 | 1 | 1 | 1
|  | 1 | 2 | 3 | 4
|  | 0 | 0 | 0 | 0